## Sheet1
# | Question | Answer
1 | Is a voluntary site visit or walkthrough available, if need be, for Building 54, Room 281 prior to proposal submission? | Yes, but not required. Currently the room is bare. Email 184WG.MSG.CONTRACTING@us.af.mil if you would like to schedule your site visit.
2 | Can the Government provide ceiling height and clearance details for the installation space? | The ceiling height in Room 281 is 10 feet from the finished floor to the suspended ceiling grid. There are no significant obstructions below the grid in the designated rack area.
3 | Are higher-resolution versions of Appendix A layout drawings available? | Yes. A higher-resolution PDF of the layout drawings will be requested from USACE.
4 | Can the Government confirm whether the L6-30R receptacles referenced are 208V or 240V? | The Government confirms the L6-30R receptacles are 208V.
5 | Are there any limitations on total electrical load capacity within the room? | While there are no specific limitations for the offeror to engineer, the room's power distribution has been designed to support the full load of the specified PDUs. Offerors should base their proposals on the PWS requirement to connect to the provided L6-30R receptacles.
6 | For the environmental monitoring system, must proposed solutions be listed on the DoDIN Approved Products List (APL) with Authority to Connect (ATC) at time of submission? | The proposed solution must be on the DoDIN APL at the time of submission. The offeror must provide evidence that the proposed system has a current or pending Authority to Connect (ATC) that will be active by the time of installation.
7 | Are “or equal” products acceptable for racks, containment systems, and PDUs if they meet or exceed specifications? | Yes
8 | Will the Government provide a designated staging area for equipment delivery and installation? | Yes. The Government will provide a designated and secure staging area within for equipment storage prior to and during the installation window. The location will be coordinated with the awarded contractor.
9 | Are there any restrictions on work hours during the installation period? | PWS section 2.3.2. states “Hours of Operation: The contractor shall normally perform all on-site work between the hours of 0730-1630 CST Monday-Friday, excluding federal holidays. However, due to the compressed on-site schedule required by this PWS, extended work hours, including nights, weekends, and federal holidays, are authorized and should be anticipated by the contractor to meet the required completion date. All extended work hours must be coordinated in advance with the COR.”
10 | Is the July 8–21 installation window firm, or is there flexibility? | The 14-calendar-day duration for on-site installation is firm and non-negotiable. The currently planned window is 08 July – 21 July 2026, and offerors shall base their proposals on this target.However, as stated in the PWS, the final start date is dependent on the completion of prior construction phases. The Government reserves the right to adjust this start date. To manage this, the Government will provide the awarded contractor with a formal, written Authorization to Proceed (ATP) no less than thirty (30) calendar days prior to the confirmed start date. The mandatory 14-day completion timeline will begin on the start date specified in that official ATP notice.
11 | Will this procurement be evaluated as Lowest Price Technically Acceptable (LPTA)? | The lowest price that meets the evaluation criteria set forth in the solicitation is being used to evaluate the quotes under FAR Part 12.
12 | Are there any past performance requirements that must be submitted with the quote? | Not required and submissions will not be evaluated
13 | 1) Please confirm the total number of data drops / CAT6 cables required under this project. | None. This project is for data center infrastructure outfitting (racks, power, containment) only. There is no requirement for the contractor to furnish or install any low-voltage data cabling (e.g., CAT6, fiber optic) under this PWS.
14 | 1) Please identify each location requiring data cabling and the number of cables required at each location. | Not Applicable. Data cabling is not part of this requirement.
15 | 1) Please confirm whether any of the requested data cables are intended to serve cameras, Wi‑Fi access points, televisions, time clocks, or other owner-furnished / contractor-furnished devices. If so, please provide the device types and any mounting-height requirements that may affect pricing and installation. | Not Applicable. Data cabling is not part of this requirement.
16 | 1) Please confirm whether racks, cabinets, ladder rack, cable tray, backboards, patch panels, and similar pathway/support components are Government-furnished or contractor-furnished. If contractor-furnished, please identify the required types, sizes, and quantities. | Per the Performance Work Statement (PWS), the contractor is required to furnish and install the following: thirty-eight (38) server/network racks and two (2) cold aisle containment systems. The specific equipment must meet the salient characteristics outlined in the PWS. The contractor is not responsible for furnishing or installing ladder rack, general facility cable tray, backboards, or patch panels under this contract.
17 | 1) Please confirm the required cable specification, including category, shielding requirements, jacket/plenum rating, termination requirements, and preferred cable color. | Not Applicable. Data cabling is not part of this requirement
18 | 1) Please confirm whether any fiber backbone, fiber patching, fiber terminations, or fiber-related hardware are required as part of this project. If yes, please provide the type of fiber, connection points, and quantities. | Not Applicable. Fiber optic cabling is not part of this requirement.
19 | Please provide the applicable PWS, salient characteristics, drawings, riser diagrams, device schedules, and/or technology plans that define the low-voltage scope in sufficient detail for bidding. | The complete scope of work is defined in the solicitation's Performance Work Statement (PWS) and its appendices, which describe an infrastructure outfitting project, not a structured cabling project. Therefore, documents such as riser diagrams and cabling schedules are not applicable to this requirement. All offerors must base their offers strictly on the PWS and its associated documents provided in the official solicitation.
20 | Please confirm room size to help establish how much cable will be needed to meet requirements. | Not Applicable
21 | Could the proposal date be extended to allow design team to do their part of the project? (Requested by Design Team). | No, with the exceptions of extinuating circumstances. With the strict timelines that are to be met, the extention of the solicitation date will result in extending the award date and potentionally increase the risk the delivery timeline.