## Qty.
Item No. | Item description | Unit | Quantity
1 | Transformer & Reactor
1.1 | 220/132 kV AUTO TRANSFORMER
a) | 53.33/66.66 MVA, 220/√3/132/√3/33 kV Single phase Auto Transformer with all fittings & accessories as specified/ required for completion of the scope of works as per technical specification | Nos. | 7
b) | Insulating oil for first filling plus 10 % extra to account for spillage, sampling etc. for all the Transformers. | Lot | 1
1.2 | 25 MVAR, 245kV, three phase, 50 Hz Bus Shunt Reactor as specified below:
a) | 25 MVAR, 245kV, three phase reactor | No. | 1
b) | Insulating oil for first filling plus 10% extra to account for spillage etc. during filling for the Shunt Reactor | Lot | 1
Sub Total (1)
2 | 245KV GIS Equipment [Module description as per technical specification, Chapter 1-PSR]
2.1 | GIS Bus Bars modules | Sets | 2
2.2 | GIS Bus Coupler bay module | Set | 1
2.3 | GIS Line feeder bay module | Sets | 6
2.4 | GIS Auto transformer bay module | Sets | 2
2.5 | GIS Bus Shunt Reactor Module | Set | 1
2.6 | SF6 GIS Auxiliary Bus Module as per PSR to connect spare unit of Transformer | Set | 1
2.7 | SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure and accessories
Option-I
i | Single phase GIB, 2000A for Line | Mtr | 210
ii | Single phase GIB, 1600A for Transformers | Mtr | 302
iii | Single phase GIB, 1600A for Reactor | Mtr | 168
Option-II
i | Three phase GIB, 2000A for Line | Mtr | 70
ii | Single phase GIB, 1600A for Transformers | Mtr | 302
iii | Three phase GIB, 1600A for Reactor | Mtr | 56
Note: Bidder is required to quote for either option-I or Option-II
2.8 | 220kV, SF6 to Air Bushing along with associated support structure
Option-I
i | Single Phase SF6 to Air Bushing | Nos. | 16
Option-II
i | Single Phase SF6 to Air Bushing for Single Phase Transformer | Nos. | 7
ii | Three Phase for Line bay | Nos. | 2
iii | Three Phase for Reactor | No. | 1
Note: Bidder is required to quote for either option-I or Option-II
2.9 | 220kV Power Cable (XLPE), Termination & Jointing Kits along with associated support structure
i | 1C*1600sq.mm Cu Power Cable (XLPE) | Mtr | 1050
ii | SF6 Switchgear type Cable end Termination & Jointing Kits | Sets | 4
iii | Outdoor Cable end Termination (including Composite/porcelain bushing) & Jointing Kits | Sets | 4
Sub Total (2)
3 | 145kV Circuit Breakers
3.1 | 1600A, 40KA, SF6 CB | Set | 1
Sub Total (3)
4 | Disconnectors/Isolators
4.1 | 145 kV Disconnectors/Isolators- Double Break
i) | 1250A, 40kA Isolator with double earthing switch | Set | 1
ii) | 1250A, 40kA Isolator without earthing switch | Sets | 2
iii) | 1250A, 40kA Isolator without earthing switch-Gantry mounted | Set | 1
iv) | 1250A, 40kA Isolator with Single earthing switch | Set | 1
v) | 1250A, 40kA Single Pole Isolator | Nos. | 5
vi) | 1250A, 40kA Single Pole Isolator with Earth Switch | Nos. | 8
4.2 | 36 kV Disconnectors/Isolators- Double Break
i) | 800A, 31.5kA Single Pole Isolator | Sets | 2
Sub Total (4)
5 | CURRENT TRANSFORMERS(CT)
5.1 | 145 kV Current Transformer (1-Phase)
i) | 1200-600-300/1-1-1-1-1A, 5 Cores | Nos. | 3
5.2 | 36 kV Current Transformer (1-Phase)
i) | 750/1-1, 2 Cores for Neutral Bus | Nos. | 2
Sub Total (5)
6 | Surge Arrester
i) | 216 kV Surge Arrestors (1-phase) | Nos. | 28
ii) | 120 kV Surge Arrestors (1-phase) | Nos. | 7
Sub Total (6)
7 | Bus post insulators/Post Insulators complete as per specifications
i) | 245 kV | Nos. | 24
ii) | 145 kV | Nos. | 14
iii) | 72.5kV | Nos. | 74
iv) | 36kV | Nos. | 10
Sub Total (7)
8 | Capacitor Voltage Transformer (CVT) & Voltage Transformer (VT)
i) | 220 kV/ √3 kV / 110/ √3V, 3 Cores | Nos. | 30
ii) | 132kV/ √3 kV / 110/ √3V, 3 cores | Nos. | 1
Sub Total (8)
9 | CONTROL & RELAY PANELS (WITH AUTOMATION)
9.1 | 245kV
9.1.1 | Circuit Breaker Control & Relay Panel
a) | Line Protection Panel (Type-I) as per technical specification | Sets | 6
9.1.2 | 220/132 kV Transformer Protection Panel (For HV, MV, LV side) as per Specification | Sets | 2
9.1.3 | Bus Bar Protection Panel (D-M Bus) | set | 1
9.1.4 | Bus coupler protection Panel | set | 1
9.1.5 | Reactor Protection Panel as per specification | set | 1
9.2 | 145kV
9.2.1 | Augmentations of Bus Bar Protection for 132 kV ICT Bays | Lot | 1
Sub Total (9)
10 | SUBSTATION AUTOMATION
10.1 | Augmentations of Existing Substation automation system including hardware and software for the substation along with associated equipment for the following Main bays to be automated as per Technical Specification and configuration of Gateways for all bays under present scope for integration of the SCADA of SIEMENS (SINAUT Spectrum) at Load Dispatch Centre, Kathmandu including supply of Hardware, Software, accessories etc. complete as per Technical Specification:
a | 220 kV System | Bays | 10
b | 132 kV System | Lot | 1
c | For Auxiliary system | Lot | 1
10.2 | Integration of all bays under the present scope and existing 132 kV bays into the SCADA system of the MCC equipped with GE Grid Solutions SCADA software, including supply, installation, configuration, testing, and commissioning of all required hardware, software, accessories, etc., complete in all respects as per the Technical Specifications | Lot | 1
Sub Total (10)
11 | Digital Protection Coupler
11.1 | Addition of Distance Protection Module required for 220 kV Basantapur- Dhungesangu Transmission Line at Basantapur and Dhungesanghu Substations in the Existing ABB (Hitachi) make FOX615 equipment at each substation to complete the Distance Teleprotection as per specifications. | Lot | 1
Sub Total (11)
12 | Visual monitoring system (VMS) system
a | Augmentations of existing Visual monitoring system (VMS) as specified/required complete in all respect including HF Cable, Other necessary cabling and power supply system for Present Scope of the Works | Lot | 1
Sub Total (12)
13 | Power & Control Cables
a | Power Cables (PVC) - (1.1kV grade) | Lot | 1
b | Power Cables (XLPE) - (1.1kV grade) | Lot | 1
c | Control Cable (PVC) - (1.1kV grade) | Lot | 1
d | Cable glands, lugs & straight through joints for Power & Control cables | Lot | 1
Sub Total (13)
14 | LT Switchgear (As per Technical specification)
a | 400V ACDB Extension | Set | 1
b | 400V ELDB Extension | Set | 1
c | 110 V DCDB | Nos. | 2
Sub Total (14)
15 | Batteries & Battery charger (The Rating of the batteries & Chargers shall be decided as per requirement of the specification and shall be worked out by Bidder)
15.1 | Batteries as per PSR
a | 110V | Sets | 2
15.2 | Float Cum Boost Battery Charger
a | 110V Float Cum Boost Battery Charger | Sets | 2
Sub Total (15)
16 | Fire Protection System
a | Nitrogen Injection Fire Protection cum extinguishing System (NIFPES) for 66.66 MVA Transformers complete in all respect as specified in technical specifications | Sets | 7
b | Portable /Trolley/Wheel mounted extinguishers
i | 9 liter water type | Nos. | 8
ii | 60 liter foam type | Nos. | 4
iii | 4.5 kg CO2 type | Nos. | 2
iv | 4.5 kg Dry Chemical Power (DCP) type | Nos. | 6
c | Smoke detection system | Set | 1
d | Fire detection and Alarm System | Set | 1
Sub Total (16)
17 | Illumination System
a | Switchyard lighting | Lot | 1
b | Street lighting | Lot | 1
Sub Total (17)
18 | Air conditioning & Ventilation system
a | High wall types split AC unit of 2 TR capacities for C&R/ACDB/Battery Room as per technical specification | Nos. | 26
b | Ventilation system for 220 kV GIS hall Building and other places as per technical specification | Lot | 1
Sub Total (18)
19 | Earthing and lightning protection including necessary Earth Conductor (copper), Earth Rod (copper clad steel), trench and other places cu flat earthing, Equipment for lightning protection, connectors/connections, risers etc. complete in all respect | Lot | 1
Sub Total (19)
20 | EOT Crane as per specification
a | EOT crane with suitable double Runway rails including trolley runway with conductors, fixtures, insulations size suitable to operate as and when required, complete with all accessories and slings as detailed in the specifications. | Set | 1
Sub Total (20)
21 | Pre-Engineered GIS/AHU/C&R/ACDB/Battery/SF6 gas storage Building
a | Supply, fabrication of M.S Structural steel as per TS to complete the works for GIS Hall/AHU/C&R/ACDB/Battery/SF6 gas storage Building | MT | 138.53
b | Other Miscellaneous item such as roof panels/wall panels etc. as per TS to complete the works | LS | 1
Sub Total (21)
22 | STEEL STRUCTURES (Tower, Gantry structures & Equipment support structures)
a | Fabrication, galvanizing and supply of following Lattice/pipe Structure for towers, beams and equipment including peak plates/pack washers and gusset paltes including foundation bolts(nuts, washers, MS plate welded at the bottom)
i) | Lattice/Pipe structures & foundation bolts | MT | 298.5
b | Fasteners for towers, beams and equipment support structures | MT | 14.93
Sub Total (22)
23 | Erection Hardware:- Insulator strings, Insulators, Hardware, conductor, bus-bar materials, AL Pipe, cable trays, Bay MB, clamps, spacers, connectors including connectors for Auto Transformer , Junction box, earth wire, buried cable trenches/pipe of equipment & lighting, all accessories etc. applicable for the following:
23.1 | 220 kV DM-type layout for GIS termination arrangement
a | Line Bay | Sets | 6
b | Transformer Bay including Neutral bus arrangement and Tertiary Delta Formation | Sets | 7
c | Reactor bay | Set | 1
23.2 | 132 kV layout for AIS
a | Transformer Bay including 220/132 kV AIS connection for spare unit arrangement as per Specification | Set | 1
b | Connection arrangement of Existing 132kV line bay to Transformer bay | Set | 1
c | Jack Bus (Bus Expansion) arrangement | Set | 1
Sub Total (23)
Total of Subtotal 1 to 23
24 | MANDATORY SPARES
I | Transformer for 220/132kV, 53.33/66.67 MVA
i) | All Bushing with gaskets etc. (each HV/IV/LV/Neutral voltage rating) for each rating | No | 1
ii) | Gaskets for all openings on Transformer tank for each rating | Set | 1
iii) | Oil and Winding Temperature Indicators. | Nos. | 6
iv) | Magnetic oil level gauge | No. | 1
v) | Pressure Relief Device | No. | 1
vi) | Oil pumps with motor & starter | No. | 1
vii) | Oil flow indicator | Nos. | 2
viii) | Contactors used in the cooler control circuit. | Nos. | 6
ix) | Relays used in the cooler control circuit. | Nos. | 6
x) | Indication lamps assembly complete used in the Marshalling box/marshalling box. | Nos. | 10
xi) | MCCBs/ MCBs used in Marshalling Box/RTCC/Panels | Nos. | 6
xii) | Buchholz Relay(Main Tank) complete with floats and contacts | Nos. | 2
xiii) | Valves of each type used | Nos. | 2
xiv) | Air cell | Nos. | 1
xv) | Neutral CTs | Nos. | 1
xvi) | Switches/ Push Buttons used in the panels | Nos. | 9
xvii) | Heater used in the panels | Nos. | 2
xviii) | Thermostat used in the panels | Nos. | 2
xix) | Terminal blocks used in the panels | Nos. | 6
xx) | Oil Surge Relay and AVR Relay | Nos. | 1
xxi) | Drive Motor for OLTC with gear assembly | Nos. | 1
xxii) | Fuses used in panels | Nos. | 9
xxiii) | Oil Sampling bottle as per TS | Nos. | 6
xxiv) | Oil Syringe as per TS | Sets | 2
xxv) | Hand Tools as per TS | Sets | 1
II | Bus Shunt Reactor
i) | All Bushing with gaskets etc. (each HV/Neutral voltage rating) for each rating | No. | 1
ii) | Local and remote WTI complete unit with sensing devices and contacts | Set | 1
iii) | Local and Remote OTI complete unit with contacts and sensing bulbs | Set | 1
iv) | Magnetic Oil Level gauge | No. | 1
v) | Pressure Relief Device | Nos. | 2
vi) | Buchholz relay complete with float and contacts | No. | 1
vii) | Flexible air cell | Set | 1
viii) | Neutral Current Transformer | Sets | 2
ix) | MCBs/MCCBs of each type used | No. | 1
x) | Sets of fuses of each type used | Sets | 3
xi) | Fan Contactors used in the cooler control circuit of each type used | Nos. | 2
xii) | Relays used in the cooler control circuit of each type used | Nos. | 2
xiii) | Indication lamps (one of each type) | Nos. | 5
III | GIS
i) | Complete GIS modules, along with enclosure, all active parts such as conductor, conductor joints, shields, end covers etc. for each type of
| ➢ Bus Bar Sections (including Bus Bar Interconnection Modules) | Set | 1
| ➢ Bus Ducts Sections (including Compensators/expansion joints/bellows) | Set | 1
| ➢ Bends | Set | 1
| ➢ SF6/Air Bushing (if applicable). | Set | 1
| ➢ Oil/SF6 Bushing (if applicable). | Set | 1
| ➢ Cable Termination kit (if applicable). | Set | 1
ii) | SF6 gas Pressure Relief Device assembly of each type | Set | 1
iii) | SF6 Pressure gauge cum switch /Density monitors and pressure switch as applicable, of each type | Set | 5
iv) | Coupling device with Hose Pipe (25m) for connecting pressure gauge cum switch to Gas handling plant of each type | Set | 2
v) | Coupling device with Hose Pipe (25m) for connecting pressure gauge cum switch to SF6 gas cylinder of each type | Set | 2
vi) | Coupling device with Hose Pipe (5m) for connecting Gas handling plant to SF6 gas cylinder | Set | 2
vii) | Rubber Gaskets, “O” Rings and Seals for SF6 gas for GIS enclosures of each type | Set | 5
viii) | Molecular filter for SF6 gas with filter bags (10 % of total weight) | Set | 1
ix) | Control Valves for SF6 gas of each type | Set | 3
x) | SF6 gas (20 % of total gas quantity) | Lot | 1
xi) | Pipe length (Copper or Steel as applicable) for SF6 Circuit of each type (if applicable) | Set | 2
xii) | Locking device to keep the Dis-connectors (Isolators) and Earthing/Fast Earthing switches in close or open position in case of removal of the driving Mechanism | Set | 2
xiii) | UHF PD Sensors of each type along with BNC Connector | Nos. | 5
xiv) | Support Insulators (gas through) of each type (complete with metal ring etc.) | Nos. | 10
xv) | Gas Barriers Insulators of each type (complete with metal ring etc.) | Nos. | 10
xvi) | SF6 to air bushing of each type complete in all respect | No. | 2
IV | 145kV SF6 CB
i) | Complete Pole of circuit breaker including pole column, interrupter, with driving mechanism and Marshaling Box but without support structure for each rating (No. of Pole) | no | 1
ii) | Rubber gaskets, `O' rings and seals ( for complete replacement of one pole of CB) | set | 1
iii) | Trip coils with resistor | nos | 8
iv) | Closing coils with resistor | nos | 4
v) | Terminal Pads & connectors | nos | 2
vi) | Molecular filter | nos | 2
vii) | Relays, Power contactors, switch fuse units, limit switches, push buttons, timers & MCB etc. (1 no. of each type) | set | 1
viii) | Pressure switches / Density monitor (1 no. of each type) | set | 1
ix) | Auxiliary switch assembly (for one pole of CB) | set | 1
V | 220kV CVT
i) | Complete PT of each type with enclosure and support Insulator etc. to enable one to one replacement of all applicable type/rating of VT by spare | No. | 1
VI | 132kV CVT
i) | Complete PT of each type with enclosure and support Insulator etc. to enable one to one replacement of all applicable type/rating of VT by spare | No. | 1
VII | 132kV CT
i) | Complete CT of each type and rating as supplied with enclosure and primary/secondary conductors and support Insulator etc. to enable one to one replacement of all applicable type/rating of CT by spare | Nos. | 2
VIII | 33kV CT
i) | Complete CT of each type and rating as supplied with enclosure and primary/secondary conductors and support Insulator etc. to enable one to one replacement of all applicable type/rating of CT by spare | Nos. | 2
IX | 145kV Isolator
i) | One complete pole including support Insulator, motor operating mechanism (MOM) with box but excluding structure of each type and rating | set | 1
ii) | Copper contact fingers for male & female contacts (for one pole of Isolator) | set | 2
iii) | Open/Close contactor assembly, timers, key interlock push button switch & auxiliary switches (for one pole of Isolator) | set | 1
iv) | Limit Switch | Nos. | 2
v) | Terminal Pads & Connectors | Nos. | 3
X | 33kV Isolator
i) | One complete pole including support Insulator, motor operating mechanism (MOM) with box but excluding structure of each type and rating | Set | 1
ii) | Copper contact fingers for male & female contacts ( for one pole of Isolator) | set | 2
iii) | Open/Close contactor assembly, timers, key interlock push button switch & auxiliary switches (for one pole of Isolator) | set | 1
iv) | Limit Switch | Nos. | 2
v) | Terminal Pads & Connectors | nos | 3
XI | 216kV LA
i) | Complete Surge arrester | No. | 1
ii) | Surge counter/ monitor of each type | No. | 2
XII | 120 kV LA
i) | Complete Surge arrester | No. | 1
ii) | Surge counter/ monitor of each type | No. | 2
XIII | Relay & Protection panel
i) | Breaker Relay Panel
a) | Breaker failure Relay | No. | 1
b) | Trip/Close Circuit Supervision Relay | No. | 2
c) | Self-reset trip relay of each type (if applicable) | No. | 1
d) | Auto Reclose relay with check synchronizing relay and dead line charging relay | No. | 1
e) | Timer relay of each type (if applicable) | No. | 1
f) | DC Supervision relays (if applicable) | No. | 1
g) | Hand reset Trip Relay of each type (if applicable) | No. | 1
h) | Flag relays of each type (if applicable) | No. | 1
i) | Master trip relay | No. | 1
j) | Auxiliary relays of each type | No. | 1
k) | DC changeover relay | No. | 1
ii) | Line Protection Panel Equipment spare
a) | Main-1 Numerical distance relay (excluding external trip relays) with software and cable for front panel communication to PC (if applicable) | Set | 1
b) | Main-2 Numerical distance relay (excluding external trip relays) with software and cable for front panel communication to PC (if applicable) | Set | 1
c) | Numerical current differential relay with inbuilt distance protection (excluding external trip relays) with software and cable for front panel communication to PC (if applicable) | Set | 1
d) | Disturbance recorder comprising of evaluation & acquisition units with software (if standalone) | Set | 1
e) | Distance to fault locator including mutual compensation units (if standalone) | Set | 1
f) | Over voltage protection relays with timers (Stage-I & Stage-II) (If standalone) | Set | 1
iii) | Transformer Protection Panel
a) | Transformer overall differential protection relay including all aux. CTs (if applicable), associated software and cable for front panel communication to PC (in case of numerical relay) | No. | 1
b) | Restricted Earth Fault protection relay with non linear resistor (if applicable) and associated software in case of numerical relay | No. | 1
c) | Back up protection relay with 3 O/C and E/F element and associated software in case of numerical relay | Set | 1
d) | Over fluxing relay (if stand alone) | Set | 1
e) | CVT fuse failure relay (if applicable) | Set | 1
f) | Over load relay with timer (if applicable) | Set | 1
iv) | Reactor Protection Panel
a) | Reactor overall differential protection relay including all aux. CTs (if applicable) , associated software and cable for front panel communication to PC ( in case of numerical relay) | No. | 1
b) | Restricted Earth Fault protection relay with non linear resistor (if applicable) and associated software in case of numerical relay | No. | 1
c) | Back up protection relay with 3 O/C and E/F element and associated software in case of numerical relay | Set | 1
d) | Over fluxing relay (if stand alone) | Set | 1
e) | CVT fuse failure relay (if applicable) | Set | 1
f) | Over load relay with timer (if applicable) | Set | 1
v) | Common Spares
a) | Busbar differential protection relay including all aux. CTs (if applicable), associated software and cable for front panel communication to PC (in case of numerical relay) | Set | 1
b) | Power supply module for Bus Bar Protection | Set | 1
c) | Metrosil (Non-Linear resistor) each type if applicable | Set | 1
d) | Inter-posing CTs & PTs each type | Set | 1
e) | Power Supply module of Event logger | No | 1
f) | Processor Card of Event logger | Set | 1
g) | Fuse and MCB used in CRP panel (2 Nos. of each type and rating) | Set | 1
XIV | Substation Automation System
i) | Bay control unit with associated software | No. | 1
ii) | Ethernet switch of each type | No. | 1
iii) | Longest optical cable with end terminations | Set | 1
iv) | FO Patch cords of each type and length used | Sets | 5
v) | Industrial RJ45 Connector | Nos. | 20
vi) | RJ45 Network Cable Crimping tool | Set | 1
vii) | Remote Terminal Unit (if applicable) | No. | 1
viii) | LIU (Light Interface Unit) box | No. | 1
ix) | KVM extender (if applicable) | Set | 1
XV | Battery and Battery Charger
i) | 110 V Battery Bank
a) | Terminal Connector with Nuts and Bolts | No. | 10
ii) | Battery charger (110V)
a) | Set of control cards | Set | 1
b) | Set of relays | Set | 1
c) | Rectifier transformer | No. | 1
d) | Thyristor/diode | Set | 2
e) | Fuses of Thyristor with indicators | Set | 6
XVI | LT Switchgear
i) | Relays of each type used | Set | 1
ii) | CTs and PTs each type used | Set | 1
iii) | Switches/ Push buttons and Meters each type used | Set | 1
iv) | TPN Switches / MCB each type used | Set | 1
v) | MCCB of each rating | Set | 1
vi) | LT Breaker Spares:
a) | Spring Charging motor | No. | 1
b) | Aux. Contact sets | Set | 2
c) | Bus Bar seal off insulators | No | 5
d) | Arc Chutes | Set | 2
e) | Moving contacts | Set | 1
f) | Arcing contacts (Fixed/Moving) | Set | 1
g) | Springs (Closing/Opening) | No. | 1
h) | Closing Coil | No. | 1
i) | Tripping Coil | No. | 1
j) | Aux. finger contact | Set | 1
k) | Limit Switches | Set | 1
l) | Jaw Contacts | Set | 1
vii) | Bus Bar Insulators | No. | 5
viii) | Interphase Barrier | No. | 2
ix) | Bus Bar Stip used | MTR | 5
XVII | Erection Hardware
i) | 5% spares of the actual quantities for Insulator strings & hardwares, clamps & connectors (including equipment connectors), spacers, corona bell and welding sleeves etc. | LS | 1
XVIII | BPI
i) | 220 kV | Nos. | 5
ii) | 132 kV | Nos. | 5
iii) | 72.5kV | Nos. | 5
iv) | 36kV | Nos. | 2
XIX | Tools and Testing Equipment
i) | Transformer oil testing (BDV) kit | Set | 1
ii) | 5 kV Digital Megger | Set | 1
iii) | Multimeter digital | Set | 1
iv) | 4 Terminal Earth tests | Set | 1
v) | Phase sequence meters | Set | 1
vi) | Portable Ladder with adjustable height as per TS | Set | 1
XX | Testing & Maintenance Equipment for 220 kV GIS
i) | SF6 Gas Processing Unit ( filling and evacuating) | Set | 1
ii) | Portable Partial Discharge Monitoring System | Set | 1
iii) | SF6 gas analyzer | Set | 1
iv) | SF6 Gas Leak Detector | Set | 1
XXI | Other/Common equipments Pertaining to C & R System
i) | Relay Tool kit | No. | 1
Sub Total (24)
TOTAL of Schedule 1 to be carried forward to Schedule No. 5: Grand Summary

## Extra to be quoted for reactors
Unit rate for the supply of Bus Shunt Reactor
Item No. | Item description | Unit | Quantity
1 | Bus Shunt Reactor
1.1 | 30 MVAR, 245kV, three phase, 50 Hz Bus Shunt Reactor as specified below:
a) | 30 MVAR, 245kV, three phase reactor | No. | 1
b) | Insulating oil for first filling plus 10% extra to account for spillage etc. during filling for the Shunt Reactor | Lot | 1
1.2 | 50 MVAR, 245kV, three phase, 50 Hz Bus Shunt Reactor as specified below:
a) | 50 MVAR, 245kV, three phase reactor | No. | 1
b) | Insulating oil for first filling plus 10% extra to account for spillage etc. during filling for the Shunt Reactor | Lot | 1
Sub Total (1)
Note : 1) Bidder is required to quote prices in this Schedule for all the individual items/sub-items and individual items. 2.) The Prices of equipments are inclusive of type test charges 3.) The Lot Items mentioned above has been accessed by the Bidder 4.) This is required only for rate purpose. This may be applied if the design requirement require above rating. The rate of installation shall be same as 25MVAR Reactor.